## Bhuj
Pump Efficiency Calculation Sheet (As Per HIS 2010)
| PROJECT | Rapar CITY WSS
| Head Works | Rapar H.W.
| System Discharge | 55 | LPS
| System Head | 30 | M
| No. of Pumps Working | 1
| Discharge / Pump | 55 | LPS
|  | 198 | M3/Hr
|  | 0.055 | M3/S
|  | Sample I |  | Sample II
| For Pumps with RPM | 1450 |  | 2900
Submerged Centrifugal Pump (Pump Description : "F" API End Suction Small)
| No. of Stages | 1 |  | 1
| No. of Suction | 1 |  | 1
| Specific speed ns = RPM x Q 0.5/ H0.75 | 27 |  | 53
| Optimum normally attainable efficiency as per chart 20.3a | 79 |  | 79
| Efficiency reduction due to specific speed as per figure 20.3b | 1.3 |  | 0.3
| Deviation from normally attainable efficiency as per figure 20.3e Minimum / Maximum | 5 |  | 5
Calculated attainable efficiency in %
| Minimum | 72.7 |  | 73.7
| Maximum | 82.7 |  | 83.7
Calculation of kilowatts rating of motor
| Water kW = (Q in LPS x H)/102 | 16.1765 |  | 16.1765
| Brake kW = Water kW/ Pump efficiency min | 22.1595 |  | 21.8601
| Reserve Power Margin @ 15 % | 25.4835 |  | 25.1391
| Selected kW of motor as per available standard rating | 30 |  | 30
Selected parameters : Q : 55 LPS, H :30 metres, Speed : 1450 RPM and 30 kW with minimum pump efficiency @ 72.70 %.
Deputy Executive Engineer
P. H. Mechanical Sub Division
BHUJ

## Friction Loss
CALCULATION FOR COEFFICIENT OF FRICTION OF VARIOUS SIZE OF PIPES BASED ON HAZEN-WILLIAMS FORMULA
Length of Pipe |  | 21 | Km |  |  |  |  | COMPARISION OF HAZEN WILLIAMS & CHEZY'S FORMULA
Diameter of pipe |  | 200 | In MM | C | Coefficient Value
Demand |  | 2.1 | In MLD | Kf | Head Loss Factor |  |  | Diameter | Velocity | Loss as per Hazen williams | Loss as per Chezy's Formula | Diff in % | Diff in 0.9 & 1.8 velocity
''C'' Value |  | 130 |  | Kd | Discharge Factor
MLD | Velocity (Mt/Sec) | Head loss per Km (Hf) | Head loss by Chezy Formula | C | Kf | Kd |  | 300 | 0.45 | 1.29 | 1.43 | 10.8527
|  |  |  | 80 | 1.511 | 0.8 |  | 300 | 0.9 | 4.5249 | 5.5171 | 21.9276
0.5 | 0.18 | 0.3679 | 0.3303 | 90 | 1.215 | 0.9 |  | 300 | 1.8 | 16.33 | 22.685 | 38.9161 | 16.9885
0.6 | 0.22 | 0.5335 | 0.4934 | 100 | 1 | 1 |  | 100 | 0.8846 | 15.75 | 15.95 | 1.2698
0.7 | 0.26 | 0.7269 | 0.6891 | 110 | 0.838 | 1.1 |  | 100 | 1.9167 | 65.96 | 74.89 | 13.5385 | 12.2687
0.8 | 0.29 | 0.8898 | 0.8573 | 120 | 0.713 | 1.2 |  | 200 | 0.92 | 7.57 | 8.65 | 14.2668
0.9 | 0.33 | 1.1304 | 1.1101 | 130 | 0.615 | 1.3 |  | 200 | 1.8 | 26.32 | 33.25 | 26.3298 | 12.0629
1 | 0.37 | 1.3972 | 1.3955 | 140 | 0.536 | 1.4 |  | 400 | 0.9 | 3.24 | 4.15 | 28.0864
1.1 | 0.41 | 1.6897 | 1.7136 | 150 | 0.472 | 1.5 |  | 400 | 1.87 | 12.62 | 17.83 | 41.2837 | 13.1973
1.2 | 0.44 | 1.9258 | 1.9735 |  |  |  |  | 500 | 0.9 | 2.5 | 3.31 | 32.4
1.3 | 0.48 | 2.2624 | 2.3486 | Value of ''C'' For Different type of pipes |  |  |  | 500 | 1.8 | 9.02 | 13.27 | 47.1175 | 14.7175
1.4 | 0.52 | 2.6239 | 2.7564
1.5 | 0.55 | 2.9111 | 3.0836
1.6 | 0.59 | 3.3153 | 3.5484 | C.I. | 100 |  |  | Pipe size In MM | MLD | Hf | Kf | Length in Km | Friction loss/Km | Total friction loss
1.7 | 0.63 | 3.7435 | 4.0459 | R.C.C. | 120
1.8 | 0.66 | 4.0803 | 4.4404 | A.C. | 130 |  |  | 200 | 2.1 | 5.4284 | 0.615 | 21 | 3.34 | 70.14
1.9 | 0.7 | 4.5501 | 4.9949 | P.V.C. | 140
2 | 0.74 | 5.0432 | 5.5821 | P.V.C. | 150 |  | Head Required | Delivery RL |  | Pumping RL |  | Diff. |  | Frinction Loss | Residual head
2.1 | 0.77 | 5.4284 | 6.0438
2.2 | 0.81 | 5.9621 | 6.6881 |  |  |  |  | 48 | - | 14.6 | = | 33.4 | + | 77.154 | 3
2.3 | 0.85 | 6.5188 | 7.3649 | CHEZY'S FORMULA
2.4 | 0.88 | 6.9512 | 7.894 | 4FLV^2/2GD |  |  | Total Head Required |  |  |  | = | 113.554 | Mtr
2.5 | 0.92 | 7.5477 | 8.6279 |  |  |  | Say total head required |  |  |  | = | 115 | Mtr
2.6 | 0.96 | 8.1666 | 9.3945
2.7 | 1 | 8.8079 | 10.1937
2.8 | 1.03 | 9.3035 | 10.8145
2.9 | 1.07 | 9.9836 | 11.6707
3 | 1.11 | 10.6857 | 12.5596
3.1 | 1.14 | 11.2267 | 13.2477
3.2 | 1.18 | 11.967 | 14.1937
3.3 | 1.22 | 12.7291 | 15.1723
3.4 | 1.25 | 13.3148 | 15.9276
3.5 | 1.29 | 14.1146 | 16.9633
3.6 | 1.33 | 14.9357 | 18.0316
3.7 | 1.36 | 15.5656 | 18.8542
3.8 | 1.4 | 16.424 | 19.9796
3.9 | 1.44 | 17.3036 | 21.1376
4 | 1.47 | 17.9771 | 22.0275
4.1 | 1.51 | 18.8934 | 23.2426
4.2 | 1.55 | 19.8307 | 24.4903
4.3 | 1.58 | 20.5473 | 25.4475
4.4 | 1.62 | 21.521 | 26.7523
4.5 | 1.66 | 22.5154 | 28.0897
4.6 | 1.7 | 23.5304 | 29.4597
4.7 | 1.73 | 24.3051 | 30.5087
4.8 | 1.77 | 25.3561 | 31.9358
4.9 | 1.81 | 26.4274 | 33.3955
5 | 1.84 | 27.2443 | 34.5117
5.1 | 1.88 | 28.3512 | 36.0285
5.2 | 1.92 | 29.4784 | 37.578
5.3 | 1.95 | 30.337 | 38.7615
5.4 | 1.99 | 31.4995 | 40.368
5.5 | 2.03 | 32.682 | 42.0071
5.6 | 2.06 | 33.5821 | 43.2579
5.7 | 2.1 | 34.7996 | 44.9541
5.8 | 2.14 | 36.037 | 46.683
5.9 | 2.17 | 36.9782 | 48.001
6 | 2.21 | 38.2503 | 49.787
6.1 | 2.25 | 39.5423 | 51.6055
6.2 | 2.29 | 40.8539 | 53.4567
6.3 | 2.32 | 41.8506 | 54.8665
6.4 | 2.36 | 43.1966 | 56.7747
6.5 | 2.4 | 44.5622 | 58.7156
6.6 | 2.43 | 45.5992 | 60.1927
6.7 | 2.47 | 46.999 | 62.1906
6.8 | 2.51 | 48.4181 | 64.2212
6.9 | 2.54 | 49.4953 | 65.7655
7 | 2.58 | 50.9484 | 67.8532
7.1 | 2.62 | 52.4208 | 69.9735
7.2 | 2.65 | 53.5378 | 71.5851
7.3 | 2.69 | 55.0439 | 73.7625
7.4 | 2.73 | 56.5692 | 75.9725
7.5 | 2.76 | 57.7258 | 77.6514
7.6 | 2.8 | 59.2846 | 79.9185
7.7 | 2.84 | 60.8625 | 82.2181
7.8 | 2.88 | 62.4595 | 84.5505
7.9 | 2.91 | 63.6697 | 86.3211
8 | 2.95 | 65.2999 | 88.7105
8.1 | 2.99 | 66.949 | 91.1325
8.2 | 3.02 | 68.1982 | 92.9704
8.3 | 3.06 | 69.8804 | 95.4495
8.4 | 3.1 | 71.5815 | 97.9613
8.5 | 3.13 | 72.8696 | 99.8665
8.6 | 3.17 | 74.6035 | 102.4353
8.7 | 3.21 | 76.3561 | 105.0367
8.8 | 3.24 | 77.6828 | 107.0092
8.9 | 3.28 | 79.4682 | 109.6677
9 | 3.32 | 81.2722 | 112.3588
9.1 | 3.35 | 82.6374 | 114.3986
9.2 | 3.39 | 84.4739 | 117.1468
9.3 | 3.43 | 86.329 | 119.9276
9.4 | 3.46 | 87.7325 | 122.0347
9.5 | 3.5 | 89.62 | 124.8726
9.6 | 3.54 | 91.5259 | 127.7431
9.7 | 3.58 | 93.4503 | 130.6463
9.8 | 3.61 | 94.9057 | 132.8451
9.9 | 3.65 | 96.8622 | 135.8053
10 | 3.69 | 98.8371 | 138.7982
10.1 | 3.72 | 100.3303 | 141.0642
10.2 | 3.76 | 102.3373 | 144.1142
10.3 | 3.8 | 104.3625 | 147.1967
10.4 | 3.83 | 105.8934 | 149.5301
10.5 | 3.87 | 107.9506 | 152.6697
10.6 | 3.91 | 110.0259 | 155.842
10.7 | 3.94 | 111.5943 | 158.2426
10.8 | 3.98 | 113.7014 | 161.472
10.9 | 4.02 | 115.8266 | 164.7339
11 | 4.05 | 117.4324 | 167.2018
11.1 | 4.09 | 119.5893 | 170.5209
11.2 | 4.13 | 121.7642 | 173.8726
11.3 | 4.17 | 123.9571 | 177.2569
11.4 | 4.2 | 125.6136 | 179.8165
11.5 | 4.24 | 127.838 | 183.2579
11.6 | 4.28 | 130.0803 | 186.7319
11.7 | 4.31 | 131.7738 | 189.3588
11.8 | 4.35 | 134.0475 | 192.8899
11.9 | 4.39 | 136.3391 | 196.4536
12 | 4.42 | 138.0695 | 199.1478
12.1 | 4.46 | 140.3922 | 202.7686
12.2 | 4.5 | 142.7329 | 206.422
12.3 | 4.53 | 144.5 | 209.1835
12.4 | 4.57 | 146.8717 | 212.894
12.5 | 4.61 | 149.2612 | 216.6371
12.6 | 4.64 | 151.0649 | 219.4659
12.7 | 4.68 | 153.4854 | 223.2661
12.8 | 4.72 | 155.9236 | 227.0989
12.9 | 4.75 | 157.7638 | 229.9949
13 | 4.79 | 160.2329 | 233.8848
13.1 | 4.83 | 162.7196 | 237.8073
13.2 | 4.87 | 165.2239 | 241.7625
13.3 | 4.9 | 167.1137 | 244.7503
13.4 | 4.94 | 169.6487 | 248.7625
13.5 | 4.98 | 172.2013 | 252.8073
13.6 | 5.01 | 174.1273 | 255.8624
13.7 | 5.05 | 176.7106 | 259.9643
13.8 | 5.09 | 179.3113 | 264.0989
13.9 | 5.12 | 181.2733 | 267.2212
14 | 5.16 | 183.9047 | 271.4128
14.1 | 5.2 | 186.5534 | 275.6371
14.2 | 5.23 | 188.5514 | 278.8267
14.3 | 5.27 | 191.2306 | 283.1081
14.4 | 5.31 | 193.9272 | 287.422
14.5 | 5.34 | 195.961 | 290.6789
14.6 | 5.38 | 198.688 | 295.0499
14.7 | 5.42 | 201.4322 | 299.4536
14.8 | 5.46 | 204.1938 | 303.8899
14.9 | 5.49 | 206.2763 | 307.2385
15 | 5.53 | 209.0682 | 311.7319
15.1 | 5.57 | 211.8772 | 316.2579
15.2 | 5.6 | 213.9954 | 319.6738
15.3 | 5.64 | 216.8346 | 324.2569
15.4 | 5.68 | 219.691 | 328.8726
15.5 | 5.71 | 221.8446 | 332.3558
15.6 | 5.75 | 224.7311 | 337.0285
15.7 | 5.79 | 227.6348 | 341.7339
15.8 | 5.82 | 229.8238 | 345.2844
15.9 | 5.86 | 232.7574 | 350.0469
16 | 5.9 | 235.7082 | 354.842
16.1 | 5.93 | 237.9325 | 358.4597
16.2 | 5.97 | 240.9131 | 363.3119
16.3 | 6.01 | 243.9108 | 368.1967
16.4 | 6.05 | 246.9256 | 373.1142
16.5 | 6.08 | 249.1978 | 376.8236
16.6 | 6.12 | 252.2423 | 381.7982
16.7 | 6.16 | 255.3039 | 386.8053
16.8 | 6.19 | 257.6112 | 390.5821
16.9 | 6.23 | 260.7024 | 395.6463
17 | 6.27 | 263.8106 | 400.7431
17.1 | 6.3 | 266.1529 | 404.5872
17.2 | 6.34 | 269.2907 | 409.7411
17.3 | 6.38 | 272.4454 | 414.9276
17.4 | 6.41 | 274.8226 | 418.8389
17.5 | 6.45 | 278.0069 | 424.0826
17.6 | 6.49 | 281.208 | 429.3588
17.7 | 6.52 | 283.62 | 433.3374
17.8 | 6.56 | 286.8506 | 438.6707
17.9 | 6.6 | 290.0981 | 444.0367
18 | 6.63 | 292.5447 | 448.0826
18.1 | 6.67 | 295.8215 | 453.5056
18.2 | 6.71 | 299.1152 | 458.9613
18.3 | 6.75 | 302.4256 | 464.4495
18.4 | 6.78 | 304.9194 | 468.5872
18.5 | 6.82 | 308.2591 | 474.1325
18.6 | 6.86 | 311.6156 | 479.7105
18.7 | 6.89 | 314.1439 | 483.9154
18.8 | 6.93 | 317.5296 | 489.5505
18.9 | 6.97 | 320.932 | 495.2181
19 | 7 | 323.4947 | 499.4903
19.1 | 7.04 | 326.9263 | 505.2151
19.2 | 7.08 | 330.3745 | 510.9725
19.3 | 7.11 | 332.9715 | 515.3119
19.4 | 7.15 | 336.4488 | 521.1264
19.5 | 7.19 | 339.9427 | 526.9735
19.6 | 7.22 | 342.5741 | 531.3802
19.7 | 7.26 | 346.097 | 537.2844
19.8 | 7.3 | 349.6365 | 543.2212
19.9 | 7.34 | 353.1926 | 549.1906
20 | 7.37 | 355.8705 | 553.6891
20.1 | 7.41 | 359.4556 | 559.7156
20.2 | 7.45 | 363.0571 | 565.7747
20.3 | 7.48 | 365.7691 | 570.3405
20.4 | 7.52 | 369.3996 | 576.4567
20.5 | 7.56 | 373.0465 | 582.6055
20.6 | 7.59 | 375.7925 | 587.2385
20.7 | 7.63 | 379.4682 | 593.4444
20.8 | 7.67 | 383.1604 | 599.683
20.9 | 7.7 | 385.9404 | 604.3833
21 | 7.74 | 389.6613 | 610.6789
21.1 | 7.78 | 393.3987 | 617.0071
21.2 | 7.81 | 396.2125 | 621.7747
21.3 | 7.85 | 399.9786 | 628.16
21.4 | 7.89 | 403.7611 | 634.578
21.5 | 7.92 | 406.6086 | 639.4128
21.6 | 7.96 | 410.4197 | 645.8879
21.7 | 8 | 414.2472 | 652.3955
21.8 | 8.04 | 418.091 | 658.9358
21.9 | 8.07 | 420.9845 | 663.8624
22 | 8.11 | 424.8569 | 670.4597
22.1 | 8.15 | 428.7455 | 677.0897
22.2 | 8.18 | 431.6727 | 682.0836
22.3 | 8.22 | 435.5898 | 688.7706
22.4 | 8.26 | 439.5233 | 695.4903
22.5 | 8.29 | 442.484 | 700.5515
22.6 | 8.33 | 446.4459 | 707.3282
22.7 | 8.37 | 450.424 | 714.1376
22.8 | 8.4 | 453.4182 | 719.2661
22.9 | 8.44 | 457.4247 | 726.1325
23 | 8.48 | 461.4474 | 733.0316
23.1 | 8.51 | 464.4751 | 738.2273
23.2 | 8.55 | 468.5261 | 745.1835
23.3 | 8.59 | 472.5934 | 752.1723
23.4 | 8.63 | 476.6767 | 759.1937
23.5 | 8.66 | 479.7499 | 764.4811
23.6 | 8.7 | 483.8615 | 771.5596
23.7 | 8.74 | 487.9893 | 778.6707
23.8 | 8.77 | 491.0957 | 784.0255
23.9 | 8.81 | 495.2517 | 791.1937
24 | 8.85 | 499.4238 | 798.3945
24.1 | 8.88 | 502.5635 | 803.8165
24.2 | 8.92 | 506.7637 | 811.0744
24.3 | 8.96 | 510.9801 | 818.3649
24.4 | 8.99 | 514.1529 | 823.8542
24.5 | 9.03 | 518.3973 | 831.2018
24.6 | 9.07 | 522.6578 | 838.5821
24.7 | 9.1 | 525.8637 | 844.1386
24.8 | 9.14 | 530.1522 | 851.5759
24.9 | 9.18 | 534.4568 | 859.0459
25 | 9.22 | 538.7773 | 866.5484
25.1 | 9.25 | 542.0283 | 872.1967
25.2 | 9.29 | 546.3768 | 879.7564
25.3 | 9.33 | 550.7414 | 887.3486
25.4 | 9.36 | 554.0252 | 893.0642
25.5 | 9.4 | 558.4177 | 900.7136
25.6 | 9.44 | 562.8261 | 908.3955
25.7 | 9.47 | 566.1429 | 914.1784
25.8 | 9.51 | 570.5792 | 921.9174
25.9 | 9.55 | 575.0315 | 929.6891
26 | 9.58 | 578.3811 | 935.5392
26.1 | 9.62 | 582.8612 | 943.368
26.2 | 9.66 | 587.3572 | 951.2294
26.3 | 9.69 | 590.7396 | 957.1468
26.4 | 9.73 | 595.2633 | 965.0652
26.5 | 9.77 | 599.803 | 973.0163
26.6 | 9.8 | 603.2181 | 979.001
26.7 | 9.84 | 607.7855 | 987.0092
26.8 | 9.88 | 612.3688 | 995.0499
26.9 | 9.92 | 616.9678 | 1003.1233
27 | 9.95 | 620.4275 | 1009.1998
27.1 | 9.99 | 625.0543 | 1017.3303
27.2 | 10.03 | 629.6968 | 1025.4934
27.3 | 10.06 | 633.1891 | 1031.6371
27.4 | 10.1 | 637.8593 | 1039.8573
27.5 | 10.14 | 642.5453 | 1048.1101
27.6 | 10.17 | 646.0702 | 1054.3211
27.7 | 10.21 | 650.7837 | 1062.631
27.8 | 10.25 | 655.5131 | 1070.9735
27.9 | 10.28 | 659.0704 | 1077.2518
28 | 10.32 | 663.8273 | 1085.6514
28.1 | 10.36 | 668.5999 | 1094.0836
28.2 | 10.39 | 672.1897 | 1100.4292
28.3 | 10.43 | 676.9899 | 1108.9185
28.4 | 10.47 | 681.8057 | 1117.4404
28.5 | 10.51 | 686.6373 | 1125.9949
28.6 | 10.54 | 690.2712 | 1132.4322
28.7 | 10.58 | 695.1302 | 1141.0438
28.8 | 10.62 | 700.0049 | 1149.6881
28.9 | 10.65 | 703.6711 | 1156.1927
29 | 10.69 | 708.5732 | 1164.894
29.1 | 10.73 | 713.4909 | 1173.6279
29.2 | 10.76 | 717.1895 | 1180.1998
29.3 | 10.8 | 722.1346 | 1188.9908
29.4 | 10.84 | 727.0953 | 1197.8145
29.5 | 10.87 | 730.8261 | 1204.4536
29.6 | 10.91 | 735.8142 | 1213.3344
29.7 | 10.95 | 740.8178 | 1222.2477
29.8 | 10.98 | 744.5808 | 1228.9541
29.9 | 11.02 | 749.6117 | 1237.9246
30 | 11.06 | 754.6582 | 1246.9276
30.1 | 11.09 | 758.4533 | 1253.7013
30.2 | 11.13 | 763.5271 | 1262.7615
30.3 | 11.17 | 768.6164 | 1271.8542
30.4 | 11.21 | 773.7213 | 1280.9796
30.5 | 11.24 | 777.5601 | 1287.8451
30.6 | 11.28 | 782.6922 | 1297.0275
30.7 | 11.32 | 787.8397 | 1306.2426
30.8 | 11.35 | 791.7106 | 1313.1753
30.9 | 11.39 | 796.8853 | 1322.4475
31 | 11.43 | 802.0756 | 1331.7523
31.1 | 11.46 | 805.9784 | 1338.7523
31.2 | 11.5 | 811.1958 | 1348.1142
31.3 | 11.54 | 816.4286 | 1357.5087
31.4 | 11.57 | 820.3634 | 1364.5759
31.5 | 11.61 | 825.6233 | 1374.0275
31.6 | 11.65 | 830.8986 | 1383.5117
31.7 | 11.68 | 834.8653 | 1390.6463
31.8 | 11.72 | 840.1677 | 1400.1876
31.9 | 11.76 | 845.4855 | 1409.7615
32 | 11.8 | 850.8188 | 1419.368
32.1 | 11.83 | 854.8289 | 1426.5943
32.2 | 11.87 | 860.1891 | 1436.2579
32.3 | 11.91 | 865.5648 | 1445.9541
32.4 | 11.94 | 869.6066 | 1453.2477
32.5 | 11.98 | 875.0092 | 1463.001
32.6 | 12.02 | 880.4272 | 1472.787
32.7 | 12.05 | 884.5008 | 1480.1478
32.8 | 12.09 | 889.9457 | 1489.9908
32.9 | 12.13 | 895.406 | 1499.8665
33 | 12.16 | 899.5113 | 1507.2946
33.1 | 12.2 | 904.9984 | 1517.2273
33.2 | 12.24 | 910.5009 | 1527.1927
33.3 | 12.27 | 914.6379 | 1534.6881
33.4 | 12.31 | 920.1672 | 1544.7105
33.5 | 12.35 | 925.7119 | 1554.7655
33.6 | 12.38 | 929.8804 | 1562.3282
33.7 | 12.42 | 935.4519 | 1572.4404
33.8 | 12.46 | 941.0386 | 1582.5851
33.9 | 12.5 | 946.6407 | 1592.7625
34 | 12.53 | 950.8523 | 1600.4169
34.1 | 12.57 | 956.4811 | 1610.6514
34.2 | 12.61 | 962.1252 | 1620.9185
34.3 | 12.64 | 966.3683 | 1628.6402
34.4 | 12.68 | 972.0392 | 1638.9643
34.5 | 12.72 | 977.7252 | 1649.3211
34.6 | 12.75 | 981.9998 | 1657.1101
34.7 | 12.79 | 987.7126 | 1667.524
34.8 | 12.83 | 993.4406 | 1677.9704
34.9 | 12.86 | 997.7466 | 1685.8267
35 | 12.9 | 1003.5013 | 1696.3303
35.1 | 12.94 | 1009.2712 | 1706.8665
35.2 | 12.97 | 1013.6086 | 1714.79
35.3 | 13.01 | 1019.4051 | 1725.3833
35.4 | 13.05 | 1025.2168 | 1736.0092
35.5 | 13.09 | 1031.0437 | 1746.6677
35.6 | 13.12 | 1035.4238 | 1754.683
35.7 | 13.16 | 1041.2773 | 1765.3986
35.8 | 13.2 | 1047.1459 | 1776.1468
35.9 | 13.23 | 1051.5574 | 1784.2294
36 | 13.27 | 1057.4526 | 1795.0347
36.1 | 13.31 | 1063.3629 | 1805.8726
36.2 | 13.34 | 1067.8056 | 1814.0224
36.3 | 13.38 | 1073.7425 | 1824.9174
36.4 | 13.42 | 1079.6945 | 1835.8451
36.5 | 13.45 | 1084.1684 | 1844.0622
36.6 | 13.49 | 1090.1468 | 1855.0469
36.7 | 13.53 | 1096.1404 | 1866.0642
36.8 | 13.56 | 1100.6455 | 1874.3486
36.9 | 13.6 | 1106.6656 | 1885.423
37 | 13.64 | 1112.7007 | 1896.5301
37.1 | 13.68 | 1118.7509 | 1907.6697
37.2 | 13.71 | 1123.2985 | 1916.0459
37.3 | 13.75 | 1129.3751 | 1927.2426
37.4 | 13.79 | 1135.4668 | 1938.472
37.5 | 13.82 | 1140.0455 | 1946.9154
37.6 | 13.86 | 1146.1636 | 1958.2018
37.7 | 13.9 | 1152.2967 | 1969.5209
37.8 | 13.93 | 1156.9065 | 1978.0316
37.9 | 13.97 | 1163.0659 | 1989.4077
38 | 14.01 | 1169.2405 | 2000.8165
38.1 | 14.04 | 1173.8812 | 2009.3945
38.2 | 14.08 | 1180.082 | 2020.8603
38.3 | 14.12 | 1186.2979 | 2032.3588
38.4 | 14.15 | 1190.9696 | 2041.0041
38.5 | 14.19 | 1197.2118 | 2052.5596
38.6 | 14.23 | 1203.4689 | 2064.1478
38.7 | 14.26 | 1208.1716 | 2072.8603
38.8 | 14.3 | 1214.455 | 2084.5056
38.9 | 14.34 | 1220.7533 | 2096.1835
39 | 14.38 | 1227.0667 | 2107.894
39.1 | 14.41 | 1231.8115 | 2116.6983
39.2 | 14.45 | 1238.1511 | 2128.4659
39.3 | 14.49 | 1244.5056 | 2140.2661
39.4 | 14.52 | 1249.2813 | 2149.1376
39.5 | 14.56 | 1255.662 | 2160.9949
39.6 | 14.6 | 1262.0577 | 2172.8848
39.7 | 14.63 | 1266.8642 | 2181.8236
39.8 | 14.67 | 1273.286 | 2193.7706
39.9 | 14.71 | 1279.7228 | 2205.7503
40 | 14.74 | 1284.5601 | 2214.7564
40.1 | 14.78 | 1291.023 | 2226.7931
40.2 | 14.82 | 1297.5008 | 2238.8624
40.3 | 14.85 | 1302.3689 | 2247.9358
40.4 | 14.89 | 1308.8727 | 2260.0622
40.5 | 14.93 | 1315.3915 | 2272.2212
40.6 | 14.97 | 1321.9251 | 2284.4128
40.7 | 15 | 1326.8352 | 2293.578
40.8 | 15.04 | 1333.3949 | 2305.8267
40.9 | 15.08 | 1339.9695 | 2318.1081
41 | 15.11 | 1344.9101 | 2327.3405
41.1 | 15.15 | 1351.5108 | 2339.6789
41.2 | 15.19 | 1358.1262 | 2352.0499
41.3 | 15.22 | 1363.0976 | 2361.3496
41.4 | 15.26 | 1369.739 | 2373.7778
41.5 | 15.3 | 1376.3954 | 2386.2385
41.6 | 15.33 | 1381.3973 | 2395.6055
41.7 | 15.37 | 1388.0796 | 2408.1233
41.8 | 15.41 | 1394.7767 | 2420.6738
41.9 | 15.44 | 1399.8093 | 2430.1081
42 | 15.48 | 1406.5323 | 2442.7156
42.1 | 15.52 | 1413.2702 | 2455.3558
42.2 | 15.55 | 1418.3333 | 2464.8573
42.3 | 15.59 | 1425.0971 | 2477.5545
42.4 | 15.63 | 1431.8757 | 2490.2844
42.5 | 15.67 | 1438.669 | 2503.0469
42.6 | 15.7 | 1443.7738 | 2512.6402
42.7 | 15.74 | 1450.593 | 2525.4597
42.8 | 15.78 | 1457.427 | 2538.3119
42.9 | 15.81 | 1462.5622 | 2547.9725
43 | 15.85 | 1469.4221 | 2560.8818
43.1 | 15.89 | 1476.2967 | 2573.8236
43.2 | 15.92 | 1481.4624 | 2583.5515
43.3 | 15.96 | 1488.3629 | 2596.5505
43.4 | 16 | 1495.2781 | 2609.5821
43.5 | 16.03 | 1500.4741 | 2619.3772
43.6 | 16.07 | 1507.4151 | 2632.4659
43.7 | 16.11 | 1514.3709 | 2645.5872
43.8 | 16.14 | 1519.5973 | 2655.4495
43.9 | 16.18 | 1526.5788 | 2668.6279
44 | 16.22 | 1533.5751 | 2681.8389
44.1 | 16.26 | 1540.586 | 2695.0826
44.2 | 16.29 | 1545.8539 | 2705.0367
44.3 | 16.33 | 1552.8905 | 2718.3374
44.4 | 16.37 | 1559.9419 | 2731.6707
44.5 | 16.4 | 1565.2401 | 2741.6922
44.6 | 16.44 | 1572.3171 | 2755.0826
44.7 | 16.48 | 1579.4089 | 2768.5056
44.8 | 16.51 | 1584.7373 | 2778.5943
44.9 | 16.55 | 1591.8548 | 2792.0744
45 | 16.59 | 1598.9869 | 2805.5872
45.1 | 16.62 | 1604.3456 | 2815.7431
45.2 | 16.66 | 1611.5034 | 2829.3129
45.3 | 16.7 | 1618.6758 | 2842.9154
45.4 | 16.73 | 1624.0647 | 2853.1386
45.5 | 16.77 | 1631.2628 | 2866.7982
45.6 | 16.81 | 1638.4755 | 2880.4903
45.7 | 16.85 | 1645.7028 | 2894.2151
45.8 | 16.88 | 1651.1329 | 2904.5301
45.9 | 16.92 | 1658.3858 | 2918.3119
46 | 16.96 | 1665.6534 | 2932.1264
46.1 | 16.99 | 1671.1136 | 2942.5087
46.2 | 17.03 | 1678.4068 | 2956.3802
46.3 | 17.07 | 1685.7145 | 2970.2844
46.4 | 17.1 | 1691.2049 | 2980.7339
46.5 | 17.14 | 1698.5381 | 2994.6952
46.6 | 17.18 | 1705.886 | 3008.6891
46.7 | 17.21 | 1711.4065 | 3019.2059
46.8 | 17.25 | 1718.7799 | 3033.2569
46.9 | 17.29 | 1726.1679 | 3047.3405
47 | 17.32 | 1731.7184 | 3057.9246
47.1 | 17.36 | 1739.1319 | 3072.0652
47.2 | 17.4 | 1746.56 | 3086.2385
47.3 | 17.43 | 1752.1405 | 3096.8899
47.4 | 17.47 | 1759.5941 | 3111.1203
47.5 | 17.51 | 1767.0621 | 3125.3833
47.6 | 17.55 | 1774.5448 | 3139.6789
47.7 | 17.58 | 1780.1663 | 3150.422
47.8 | 17.62 | 1787.6743 | 3164.7747
47.9 | 17.66 | 1795.1969 | 3179.16
48 | 17.69 | 1800.8484 | 3189.9704
48.1 | 17.73 | 1808.3964 | 3204.4128
48.2 | 17.77 | 1815.959 | 3218.8879
48.3 | 17.8 | 1821.6404 | 3229.7655
48.4 | 17.84 | 1829.2284 | 3244.2977
48.5 | 17.88 | 1836.8308 | 3258.8624
48.6 | 17.91 | 1842.5422 | 3269.8073
48.7 | 17.95 | 1850.17 | 3284.4292
48.8 | 17.99 | 1857.8123 | 3299.0836
48.9 | 18.02 | 1863.5535 | 3310.0958
49 | 18.06 | 1871.2212 | 3324.8073
49.1 | 18.1 | 1878.9034 | 3339.5515
49.2 | 18.14 | 1886.6 | 3354.3282
49.3 | 18.17 | 1892.3819 | 3365.4322
49.4 | 18.21 | 1900.1039 | 3380.2661
49.5 | 18.25 | 1907.8403 | 3395.1325
49.6 | 18.28 | 1913.6521 | 3406.3038
49.7 | 18.32 | 1921.4138 | 3421.2273
49.8 | 18.36 | 1929.1899 | 3436.1835
49.9 | 18.39 | 1935.0315 | 3447.422
50 | 18.43 | 1942.833 | 3462.4353
50.1 | 18.47 | 1950.6488 | 3477.4811
50.2 | 18.5 | 1956.5202 | 3488.787
50.3 | 18.54 | 1964.3613 | 3503.8899
50.4 | 18.58 | 1972.2169 | 3519.0255
50.5 | 18.61 | 1978.118 | 3530.3986
50.6 | 18.65 | 1985.9988 | 3545.5912
50.7 | 18.69 | 1993.894 | 3560.8165
50.8 | 18.72 | 1999.8248 | 3572.2569
50.9 | 18.76 | 2007.7452 | 3587.5392
51 | 18.8 | 2015.68 | 3602.8542
51.1 | 18.84 | 2023.6292 | 3618.2018
51.2 | 18.87 | 2029.6005 | 3629.7339
51.3 | 18.91 | 2037.5749 | 3645.1386
51.4 | 18.95 | 2045.5636 | 3660.5759
51.5 | 18.98 | 2051.5646 | 3672.1753
51.6 | 19.02 | 2059.5786 | 3687.6697
51.7 | 19.06 | 2067.6068 | 3703.1967
51.8 | 19.09 | 2073.6375 | 3714.8634
51.9 | 19.13 | 2081.6909 | 3730.4475
52 | 19.17 | 2089.7587 | 3746.0642
52.1 | 19.2 | 2095.8189 | 3757.7982
52.2 | 19.24 | 2103.9118 | 3773.472
52.3 | 19.28 | 2112.019 | 3789.1784
52.4 | 19.31 | 2118.1089 | 3800.9796
52.5 | 19.35 | 2126.2412 | 3816.7431
52.6 | 19.39 | 2134.3878 | 3832.5392
52.7 | 19.43 | 2142.5488 | 3848.368
52.8 | 19.46 | 2148.679 | 3860.261
52.9 | 19.5 | 2156.865 | 3876.1468
53 | 19.54 | 2165.0654 | 3892.0652
53.1 | 19.57 | 2171.2251 | 3904.0255
53.2 | 19.61 | 2179.4505 | 3920.001
53.3 | 19.65 | 2187.6902 | 3936.0092
53.4 | 19.68 | 2193.8794 | 3948.0367
53.5 | 19.72 | 2202.1441 | 3964.1019
53.6 | 19.76 | 2210.4231 | 3980.1998
53.7 | 19.79 | 2216.6418 | 3992.2946
53.8 | 19.83 | 2224.9458 | 4008.4495
53.9 | 19.87 | 2233.2641 | 4024.6371
54 | 19.9 | 2239.5123 | 4036.7992
54.1 | 19.94 | 2247.8555 | 4053.0438
54.2 | 19.98 | 2256.2131 | 4069.3211
54.3 | 20.02 | 2264.5849 | 4085.631
54.4 | 20.05 | 2270.8732 | 4097.8848
54.5 | 20.09 | 2279.27 | 4114.2518
54.6 | 20.13 | 2287.681 | 4130.6514
54.7 | 20.16 | 2293.9986 | 4142.9725
54.8 | 20.2 | 2302.4346 | 4159.4292
54.9 | 20.24 | 2310.8848 | 4175.9185
55 | 20.27 | 2317.2318 | 4188.3068
55.1 | 20.31 | 2325.707 | 4204.8532
55.2 | 20.35 | 2334.1963 | 4221.4322
55.3 | 20.38 | 2340.5727 | 4233.8879
55.4 | 20.42 | 2349.0869 | 4250.524
55.5 | 20.46 | 2357.6154 | 4267.1927
55.6 | 20.49 | 2364.0211 | 4279.7156
55.7 | 20.53 | 2372.5744 | 4296.4414
55.8 | 20.57 | 2381.142 | 4313.1998
55.9 | 20.6 | 2387.577 | 4325.79
56 | 20.64 | 2396.1694 | 4342.6055
56.1 | 20.68 | 2404.776 | 4359.4536
56.2 | 20.72 | 2413.3968 | 4376.3344
56.3 | 20.75 | 2419.8717 | 4389.0163
56.4 | 20.79 | 2428.5173 | 4405.9541
56.5 | 20.83 | 2437.1771 | 4422.9246
56.6 | 20.86 | 2443.6813 | 4435.6738
56.7 | 20.9 | 2452.3659 | 4452.7013
56.8 | 20.94 | 2461.0647 | 4469.7615
56.9 | 20.97 | 2467.5981 | 4482.578
57 | 21.01 | 2476.3217 | 4499.6952
57.1 | 21.05 | 2485.0594 | 4516.8451
57.2 | 21.08 | 2491.622 | 4529.7288
57.3 | 21.12 | 2500.3845 | 4546.9358
57.4 | 21.16 | 2509.1611 | 4564.1753
57.5 | 21.19 | 2515.7529 | 4577.1264
57.6 | 21.23 | 2524.5543 | 4594.423
57.7 | 21.27 | 2533.3699 | 4611.7523
57.8 | 21.31 | 2542.1995 | 4629.1142
57.9 | 21.34 | 2548.8311 | 4642.157
58 | 21.38 | 2557.6855 | 4659.5759
58.1 | 21.42 | 2566.554 | 4677.0275
58.2 | 21.45 | 2573.2146 | 4690.1376
58.3 | 21.49 | 2582.1079 | 4707.6463
58.4 | 21.53 | 2591.0152 | 4725.1876
58.5 | 21.56 | 2597.705 | 4738.3649
58.6 | 21.6 | 2606.637 | 4755.9633
58.7 | 21.64 | 2615.5831 | 4773.5943
58.8 | 21.67 | 2622.3019 | 4786.8389
58.9 | 21.71 | 2631.2727 | 4804.527
59 | 21.75 | 2640.2576 | 4822.2477
59.1 | 21.78 | 2647.0055 | 4835.5596
59.2 | 21.82 | 2656.0151 | 4853.3374
59.3 | 21.86 | 2665.0387 | 4871.1478
59.4 | 21.89 | 2671.8156 | 4884.527
59.5 | 21.93 | 2680.8639 | 4902.3945
59.6 | 21.97 | 2689.9262 | 4920.2946
59.7 | 22.01 | 2699.0026 | 4938.2273
59.8 | 22.04 | 2705.8191 | 4951.6983
59.9 | 22.08 | 2714.9201 | 4969.6881
60 | 22.12 | 2724.0351 | 4987.7105
60.1 | 22.15 | 2730.8806 | 5001.2487
60.2 | 22.19 | 2740.0203 | 5019.3282
60.3 | 22.23 | 2749.1739 | 5037.4404
60.4 | 22.26 | 2756.0484 | 5051.0459
60.5 | 22.3 | 2765.2266 | 5069.2151
60.6 | 22.34 | 2774.4189 | 5087.4169
60.7 | 22.37 | 2781.3223 | 5101.0897
60.8 | 22.41 | 2790.5392 | 5119.3486
60.9 | 22.45 | 2799.77 | 5137.6402
61 | 22.48 | 2806.7024 | 5151.3802
61.1 | 22.52 | 2815.9578 | 5169.7288
61.2 | 22.56 | 2825.2272 | 5188.1101
61.3 | 22.6 | 2834.5106 | 5206.524
61.4 | 22.63 | 2841.4824 | 5220.3558
61.5 | 22.67 | 2850.7903 | 5238.8267
61.6 | 22.71 | 2860.1122 | 5257.3303
61.7 | 22.74 | 2867.1128 | 5271.2294
61.8 | 22.78 | 2876.4593 | 5289.79
61.9 | 22.82 | 2885.8197 | 5308.3833
62 | 22.85 | 2892.8492 | 5322.3496
62.1 | 22.89 | 2902.2341 | 5341
62.2 | 22.93 | 2911.6329 | 5359.683
62.3 | 22.96 | 2918.6912 | 5373.7166
62.4 | 23 | 2928.1146 | 5392.4567
62.5 | 23.04 | 2937.5519 | 5411.2294
62.6 | 23.07 | 2944.639 | 5425.3303
62.7 | 23.11 | 2954.1007 | 5444.16
62.8 | 23.15 | 2963.5764 | 5463.0224
62.9 | 23.19 | 2973.0661 | 5481.9174
63 | 23.22 | 2980.1925 | 5496.1101
63.1 | 23.26 | 2989.7066 | 5515.0622
63.2 | 23.3 | 2999.2346 | 5534.0469
63.3 | 23.33 | 3006.3897 | 5548.3068
63.4 | 23.37 | 3015.9422 | 5567.3486
63.5 | 23.41 | 3025.5085 | 5586.423
63.6 | 23.44 | 3032.6924 | 5600.7503
63.7 | 23.48 | 3042.2832 | 5619.8818
63.8 | 23.52 | 3051.8878 | 5639.0459
63.9 | 23.55 | 3059.1005 | 5653.4404
64 | 23.59 | 3068.7295 | 5672.6616
64.1 | 23.63 | 3078.3725 | 5691.9154
64.2 | 23.66 | 3085.6138 | 5706.3772
64.3 | 23.7 | 3095.2811 | 5725.6881
64.4 | 23.74 | 3104.9623 | 5745.0316
64.5 | 23.77 | 3112.2324 | 5759.5607
64.6 | 23.81 | 3121.9379 | 5778.9613
64.7 | 23.85 | 3131.6573 | 5798.3945
64.8 | 23.89 | 3141.3907 | 5817.8603
64.9 | 23.92 | 3148.6998 | 5832.4811
65 | 23.96 | 3158.4574 | 5852.0041
65.1 | 24 | 3168.229 | 5871.5596
65.2 | 24.03 | 3175.5667 | 5886.2477
65.3 | 24.07 | 3185.3626 | 5905.8603
65.4 | 24.11 | 3195.1723 | 5925.5056
65.5 | 24.14 | 3202.5386 | 5940.261
65.6 | 24.18 | 3212.3726 | 5959.9633
65.7 | 24.22 | 3222.2205 | 5979.6983
65.8 | 24.25 | 3229.6154 | 5994.5209
65.9 | 24.29 | 3239.4876 | 6014.3129
66 | 24.33 | 3249.3735 | 6034.1376
66.1 | 24.36 | 3256.7971 | 6049.0275
66.2 | 24.4 | 3266.7073 | 6068.9093
66.3 | 24.44 | 3276.6314 | 6088.8236
66.4 | 24.48 | 3286.5693 | 6108.7706
66.5 | 24.51 | 3294.0318 | 6123.7523
66.6 | 24.55 | 3303.9939 | 6143.7564
66.7 | 24.59 | 3313.9699 | 6163.7931
66.8 | 24.62 | 3321.4609 | 6178.842
66.9 | 24.66 | 3331.4611 | 6198.9358
67 | 24.7 | 3341.4751 | 6219.0622
67.1 | 24.73 | 3348.9946 | 6234.1784
67.2 | 24.77 | 3359.0328 | 6254.3619
67.3 | 24.81 | 3369.0848 | 6274.578
67.4 | 24.84 | 3376.6329 | 6289.7615
67.5 | 24.88 | 3386.7091 | 6310.0347
67.6 | 24.92 | 3396.7991 | 6330.3405
67.7 | 24.95 | 3404.3756 | 6345.5912
67.8 | 24.99 | 3414.4898 | 6365.9541
67.9 | 25.03 | 3424.6177 | 6386.3496
68 | 25.06 | 3432.2227 | 6401.6677
68.1 | 25.1 | 3442.3748 | 6422.1203
68.2 | 25.14 | 3452.5407 | 6442.6055
68.3 | 25.18 | 3462.7203 | 6463.1233
68.4 | 25.21 | 3470.3641 | 6478.5331
68.5 | 25.25 | 3480.5679 | 6499.1081
68.6 | 25.29 | 3490.7855 | 6519.7156
68.7 | 25.32 | 3498.4577 | 6535.1927
68.8 | 25.36 | 3508.6994 | 6555.8573
68.9 | 25.4 | 3518.9548 | 6576.5545
69 | 25.43 | 3526.6554 | 6592.0989
69.1 | 25.47 | 3536.935 | 6612.8532
69.2 | 25.51 | 3547.2283 | 6633.6402
69.3 | 25.54 | 3554.9573 | 6649.2518
69.4 | 25.58 | 3565.2746 | 6670.0958
69.5 | 25.62 | 3575.6057 | 6690.9725
69.6 | 25.65 | 3583.3631 | 6706.6514
69.7 | 25.69 | 3593.7183 | 6727.5851
69.8 | 25.73 | 3604.0872 | 6748.5515
69.9 | 25.77 | 3614.4699 | 6769.5505
70 | 25.8 | 3622.2659 | 6785.3211
70.1 | 25.84 | 3632.6726 | 6806.3772
70.2 | 25.88 | 3643.093 | 6827.4659
70.3 | 25.91 | 3650.9174 | 6843.3038
70.4 | 25.95 | 3661.3618 | 6864.4495
70.5 | 25.99 | 3671.82 | 6885.6279
70.6 | 26.02 | 3679.6726 | 6901.5331
70.7 | 26.06 | 3690.1548 | 6922.7686
70.8 | 26.1 | 3700.6507 | 6944.0367
70.9 | 26.13 | 3708.5316 | 6960.0092
71 | 26.17 | 3719.0515 | 6981.3344
71.1 | 26.21 | 3729.5851 | 7002.6922
71.2 | 26.24 | 3737.4943 | 7018.7319
71.3 | 26.28 | 3748.0519 | 7040.1468
71.4 | 26.32 | 3758.6232 | 7061.5943
71.5 | 26.35 | 3766.5606 | 7077.7013
71.6 | 26.39 | 3777.1559 | 7099.2059
71.7 | 26.43 | 3787.7648 | 7120.7431
71.8 | 26.47 | 3798.3874 | 7142.3129
71.9 | 26.5 | 3806.3634 | 7158.5117
72 | 26.54 | 3817.0099 | 7180.1386
72.1 | 26.58 | 3827.6702 | 7201.7982
72.2 | 26.61 | 3835.6743 | 7218.0642
72.3 | 26.65 | 3846.3585 | 7239.7808
72.4 | 26.69 | 3857.0563 | 7261.5301
72.5 | 26.72 | 3865.0887 | 7277.8634
72.6 | 26.76 | 3875.8104 | 7299.6697
72.7 | 26.8 | 3886.5458 | 7321.5087
72.8 | 26.83 | 3894.6063 | 7337.9093
72.9 | 26.87 | 3905.3656 | 7359.8053
73 | 26.91 | 3916.1386 | 7381.7339
73.1 | 26.94 | 3924.2273 | 7398.2018
73.2 | 26.98 | 3935.0241 | 7420.1876
73.3 | 27.02 | 3945.8346 | 7442.2059
73.4 | 27.06 | 3956.6587 | 7464.2569
73.5 | 27.09 | 3964.7858 | 7480.8165
73.6 | 27.13 | 3975.6338 | 7502.9246
73.7 | 27.17 | 3986.4954 | 7525.0652
73.8 | 27.2 | 3994.6506 | 7541.6922
73.9 | 27.24 | 4005.5361 | 7563.8899
74 | 27.28 | 4016.4352 | 7586.1203
74.1 | 27.31 | 4024.6184 | 7602.8145
74.2 | 27.35 | 4035.5414 | 7625.1019
74.3 | 27.39 | 4046.4779 | 7647.422
74.4 | 27.42 | 4054.6893 | 7664.1835
74.5 | 27.46 | 4065.6497 | 7686.5607
74.6 | 27.5 | 4076.6237 | 7708.9704
74.7 | 27.53 | 4084.8631 | 7725.7992
74.8 | 27.57 | 4095.8609 | 7748.2661
74.9 | 27.61 | 4106.8723 | 7770.7655
75 | 27.65 | 4117.8973 | 7793.2977
75.1 | 27.68 | 4126.175 | 7810.2181
75.2 | 27.72 | 4137.2237 | 7832.8073
75.3 | 27.76 | 4148.2861 | 7855.4292
75.4 | 27.79 | 4156.5918 | 7872.4169
75.5 | 27.83 | 4167.678 | 7895.0958
75.6 | 27.87 | 4178.7777 | 7917.8073
75.7 | 27.9 | 4187.1114 | 7934.8624
75.8 | 27.94 | 4198.2349 | 7957.631
75.9 | 27.98 | 4209.372 | 7980.4322
76 | 28.01 | 4217.7337 | 7997.5545
76.1 | 28.05 | 4228.8945 | 8020.4128
76.2 | 28.09 | 4240.0689 | 8043.3038
76.3 | 28.12 | 4248.4586 | 8060.4934
76.4 | 28.16 | 4259.6567 | 8083.4414
76.5 | 28.2 | 4270.8683 | 8106.422
76.6 | 28.23 | 4279.286 | 8123.6789
76.7 | 28.27 | 4290.5214 | 8146.7166
76.8 | 28.31 | 4301.7703 | 8169.787
76.9 | 28.35 | 4313.0328 | 8192.8899
77 | 28.38 | 4321.4886 | 8210.2385
77.1 | 28.42 | 4332.7748 | 8233.3986
77.2 | 28.46 | 4344.0745 | 8256.5912
77.3 | 28.49 | 4352.5582 | 8274.0071
77.4 | 28.53 | 4363.8816 | 8297.2569
77.5 | 28.57 | 4375.2185 | 8320.5392
77.6 | 28.6 | 4383.7301 | 8338.0224
77.7 | 28.64 | 4395.0908 | 8361.3619
77.8 | 28.68 | 4406.4649 | 8384.7339
77.9 | 28.71 | 4415.0044 | 8402.2844
78 | 28.75 | 4426.4022 | 8425.7136
78.1 | 28.79 | 4437.8135 | 8449.1753
78.2 | 28.82 | 4446.3809 | 8466.7931
78.3 | 28.86 | 4457.8159 | 8490.3119
78.4 | 28.9 | 4469.2643 | 8513.8634
78.5 | 28.94 | 4480.7263 | 8537.4475
78.6 | 28.97 | 4489.3317 | 8555.157
78.7 | 29.01 | 4500.8173 | 8578.7982
78.8 | 29.05 | 4512.3164 | 8602.472
78.9 | 29.08 | 4520.9496 | 8620.2487
79 | 29.12 | 4532.4723 | 8643.9796
79.1 | 29.16 | 4544.0086 | 8667.7431
79.2 | 29.19 | 4552.6696 | 8685.5872
79.3 | 29.23 | 4564.2294 | 8709.4077
79.4 | 29.27 | 4575.8027 | 8733.261
79.5 | 29.3 | 4584.4915 | 8751.1723
79.6 | 29.34 | 4596.0884 | 8775.0826
79.7 | 29.38 | 4607.6988 | 8799.0255
79.8 | 29.41 | 4616.4154 | 8817.0041
79.9 | 29.45 | 4628.0494 | 8841.0041
80 | 29.49 | 4639.6968 | 8865.0367
80.1 | 29.52 | 4648.4412 | 8883.0826
80.2 | 29.56 | 4660.1122 | 8907.1723
80.3 | 29.6 | 4671.7966 | 8931.2946
80.4 | 29.64 | 4683.4945 | 8955.4495
80.5 | 29.67 | 4692.2768 | 8973.5872
80.6 | 29.71 | 4703.9982 | 8997.7992
80.7 | 29.75 | 4715.7331 | 9022.0438
80.8 | 29.78 | 4724.5431 | 9040.2487
80.9 | 29.82 | 4736.3015 | 9064.5505
81 | 29.86 | 4748.0734 | 9088.8848
81.1 | 29.89 | 4756.9111 | 9107.157
81.2 | 29.93 | 4768.7065 | 9131.5484
81.3 | 29.97 | 4780.5154 | 9155.9725
81.4 | 30 | 4789.3808 | 9174.3119
81.5 | 30.04 | 4801.2131 | 9198.7931
81.6 | 30.08 | 4813.0589 | 9223.3068
81.7 | 30.11 | 4821.952 | 9241.7136
81.8 | 30.15 | 4833.8213 | 9266.2844
81.9 | 30.19 | 4845.704 | 9290.8879
82 | 30.23 | 4857.6001 | 9315.524
82.1 | 30.26 | 4866.5309 | 9334.0224
82.2 | 30.3 | 4878.4505 | 9358.7156
82.3 | 30.34 | 4890.3835 | 9383.4414
82.4 | 30.37 | 4899.342 | 9402.0071
82.5 | 30.41 | 4911.2985 | 9426.79
82.6 | 30.45 | 4923.2684 | 9451.6055
82.7 | 30.48 | 4932.2545 | 9470.2385
82.8 | 30.52 | 4944.2479 | 9495.1111
82.9 | 30.56 | 4956.2546 | 9520.0163
83 | 30.59 | 4965.2684 | 9538.7166
83.1 | 30.63 | 4977.2985 | 9563.6789
83.2 | 30.67 | 4989.3421 | 9588.6738
83.3 | 30.7 | 4998.3835 | 9607.4414
83.4 | 30.74 | 5010.4505 | 9632.4934
83.5 | 30.78 | 5022.5308 | 9657.578
83.6 | 30.82 | 5034.6245 | 9682.6952
83.7 | 30.85 | 5043.7036 | 9701.5545
83.8 | 30.89 | 5055.8207 | 9726.7288
83.9 | 30.93 | 5067.9512 | 9751.9358
84 | 30.96 | 5077.0579 | 9770.8624
84.1 | 31 | 5089.2118 | 9796.1264
84.2 | 31.04 | 5101.3791 | 9821.423
84.3 | 31.07 | 5110.5133 | 9840.4169
84.4 | 31.11 | 5122.704 | 9865.7706
84.5 | 31.15 | 5134.908 | 9891.157
84.6 | 31.18 | 5144.0698 | 9910.2181
84.7 | 31.22 | 5156.2971 | 9935.6616
84.8 | 31.26 | 5168.5379 | 9961.1376
84.9 | 31.29 | 5177.7272 | 9980.2661
85 | 31.33 | 5189.9913 | 10005.7992
85.1 | 31.37 | 5202.2688 | 10031.3649
85.2 | 31.4 | 5211.4856 | 10050.5607
85.3 | 31.44 | 5223.7864 | 10076.1835
85.4 | 31.48 | 5236.1005 | 10101.8389
85.5 | 31.52 | 5248.428 | 10127.527
85.6 | 31.55 | 5257.6824 | 10146.8145
85.7 | 31.59 | 5270.0332 | 10172.5596
85.8 | 31.63 | 5282.3973 | 10198.3374
85.9 | 31.66 | 5291.6791 | 10217.6922
86 | 31.7 | 5304.0666 | 10243.527
86.1 | 31.74 | 5316.4674 | 10269.3945
86.2 | 31.77 | 5325.7767 | 10288.8165
86.3 | 31.81 | 5338.2008 | 10314.7411
86.4 | 31.85 | 5350.6382 | 10340.6983
86.5 | 31.88 | 5359.975 | 10360.1876
86.6 | 31.92 | 5372.4356 | 10386.2018
86.7 | 31.96 | 5384.9097 | 10412.2487
86.8 | 31.99 | 5394.2739 | 10431.8053
86.9 | 32.03 | 5406.7712 | 10457.9093
87 | 32.07 | 5419.2818 | 10484.0459
87.1 | 32.11 | 5431.8057 | 10510.2151
87.2 | 32.14 | 5441.2073 | 10529.8634
87.3 | 32.18 | 5453.7545 | 10556.0897
87.4 | 32.22 | 5466.3149 | 10582.3486
87.5 | 32.25 | 5475.744 | 10602.0642
87.6 | 32.29 | 5488.3277 | 10628.3802
87.7 | 32.33 | 5500.9247 | 10654.7288
87.8 | 32.36 | 5510.3811 | 10674.5117
87.9 | 32.4 | 5523.0014 | 10700.9174
88 | 32.44 | 5535.6349 | 10727.3558
88.1 | 32.47 | 5545.1187 | 10747.2059
88.2 | 32.51 | 5557.7755 | 10773.7013
88.3 | 32.55 | 5570.4455 | 10800.2294
88.4 | 32.58 | 5579.9567 | 10820.1468
88.5 | 32.62 | 5592.65 | 10846.7319
88.6 | 32.66 | 5605.3565 | 10873.3496
88.7 | 32.69 | 5614.8951 | 10893.3344
88.8 | 32.73 | 5627.6248 | 10920.0092
88.9 | 32.77 | 5640.3678 | 10946.7166
89 | 32.81 | 5653.124 | 10973.4567
89.1 | 32.84 | 5662.6999 | 10993.5331
89.2 | 32.88 | 5675.4793 | 11020.3303
89.3 | 32.92 | 5688.272 | 11047.16
89.4 | 32.95 | 5697.8752 | 11067.3038
89.5 | 32.99 | 5710.691 | 11094.1906
89.6 | 33.03 | 5723.5201 | 11121.1101
89.7 | 33.06 | 5733.1507 | 11141.3211
89.8 | 33.1 | 5746.0029 | 11168.2977
89.9 | 33.14 | 5758.8684 | 11195.3068
90 | 33.17 | 5768.5263 | 11215.5851
90.1 | 33.21 | 5781.4149 | 11242.6514
90.2 | 33.25 | 5794.3168 | 11269.7503
90.3 | 33.28 | 5804.0019 | 11290.0958
90.4 | 33.32 | 5816.927 | 11317.2518
90.5 | 33.36 | 5829.8653 | 11344.4404
90.6 | 33.4 | 5842.8168 | 11371.6616
90.7 | 33.43 | 5852.5391 | 11392.0989
90.8 | 33.47 | 5865.5137 | 11419.3772
90.9 | 33.51 | 5878.5015 | 11446.6881
91 | 33.54 | 5888.2511 | 11467.1927
91.1 | 33.58 | 5901.2621 | 11494.5607
91.2 | 33.62 | 5914.2862 | 11521.9613
91.3 | 33.65 | 5924.063 | 11542.5331
91.4 | 33.69 | 5937.1103 | 11569.9908
91.5 | 33.73 | 5950.1708 | 11597.4811
91.6 | 33.76 | 5959.9749 | 11618.1203
91.7 | 33.8 | 5973.0584 | 11645.6677
91.8 | 33.84 | 5986.1552 | 11673.2477
91.9 | 33.87 | 5995.9865 | 11693.9541
92 | 33.91 | 6009.1064 | 11721.5912
92.1 | 33.95 | 6022.2394 | 11749.261
92.2 | 33.99 | 6035.3857 | 11776.9633
92.3 | 34.02 | 6045.254 | 11797.7615
92.4 | 34.06 | 6058.4233 | 11825.5209
92.5 | 34.1 | 6071.6058 | 11853.3129
92.6 | 34.13 | 6081.5014 | 11874.1784
92.7 | 34.17 | 6094.7069 | 11902.0275
92.8 | 34.21 | 6107.9257 | 11929.9093
92.9 | 34.24 | 6117.8484 | 11950.842
93 | 34.28 | 6131.0902 | 11978.7808
93.1 | 34.32 | 6144.3451 | 12006.7523
93.2 | 34.35 | 6154.295 | 12027.7523
93.3 | 34.39 | 6167.573 | 12055.7808
93.4 | 34.43 | 6180.8642 | 12083.842
93.5 | 34.46 | 6190.8412 | 12104.9093
93.6 | 34.5 | 6204.1554 | 12133.0275
93.7 | 34.54 | 6217.4827 | 12161.1784
93.8 | 34.57 | 6227.4868 | 12182.3129
93.9 | 34.61 | 6240.8372 | 12210.5209
94 | 34.65 | 6254.2007 | 12238.7615
94.1 | 34.69 | 6267.5774 | 12267.0347
94.2 | 34.72 | 6277.6185 | 12288.261
94.3 | 34.76 | 6291.0182 | 12316.5912
94.4 | 34.8 | 6304.431 | 12344.9541
94.5 | 34.83 | 6314.4992 | 12366.2477
94.6 | 34.87 | 6327.935 | 12394.6677
94.7 | 34.91 | 6341.384 | 12423.1203
94.8 | 34.94 | 6351.4793 | 12444.4811
94.9 | 34.98 | 6364.9512 | 12472.9908
95 | 35.02 | 6378.4363 | 12501.5331
95.1 | 35.05 | 6388.5587 | 12522.9613
95.2 | 35.09 | 6402.0667 | 12551.5607
95.3 | 35.13 | 6415.5878 | 12580.1927
95.4 | 35.16 | 6425.7373 | 12601.6881
95.5 | 35.2 | 6439.2814 | 12630.3772
95.6 | 35.24 | 6452.8386 | 12659.0989
95.7 | 35.28 | 6466.409 | 12687.8532
95.8 | 35.31 | 6476.5953 | 12709.4404
95.9 | 35.35 | 6490.1886 | 12738.2518
96 | 35.39 | 6503.795 | 12767.0958
96.1 | 35.42 | 6514.0084 | 12788.7503
96.2 | 35.46 | 6527.6377 | 12817.6514
96.3 | 35.5 | 6541.2801 | 12846.5851
96.4 | 35.53 | 6551.5206 | 12868.3068
96.5 | 35.57 | 6565.1859 | 12897.2977
96.6 | 35.61 | 6578.8644 | 12926.3211
96.7 | 35.64 | 6589.1318 | 12948.1101
96.8 | 35.68 | 6602.8332 | 12977.1906
96.9 | 35.72 | 6616.5476 | 13006.3038
97 | 35.75 | 6626.842 | 13028.16
97.1 | 35.79 | 6640.5794 | 13057.3303
97.2 | 35.83 | 6654.3298 | 13086.5331
97.3 | 35.86 | 6664.6513 | 13108.4567
97.4 | 35.9 | 6678.4246 | 13137.7166
97.5 | 35.94 | 6692.211 | 13167.0092
97.6 | 35.98 | 6706.0105 | 13196.3344
97.7 | 36.01 | 6716.3687 | 13218.3496
97.8 | 36.05 | 6730.1911 | 13247.7319
97.9 | 36.09 | 6744.0265 | 13277.1468
98 | 36.12 | 6754.4117 | 13299.2294
98.1 | 36.16 | 6768.27 | 13328.7013
98.2 | 36.2 | 6782.1414 | 13358.2059
98.3 | 36.23 | 6792.5535 | 13380.3558
98.4 | 36.27 | 6806.4477 | 13409.9174
98.5 | 36.31 | 6820.355 | 13439.5117
98.6 | 36.34 | 6830.7941 | 13461.7288
98.7 | 36.38 | 6844.7242 | 13491.3802
98.8 | 36.42 | 6858.6674 | 13521.0642
98.9 | 36.45 | 6869.1334 | 13543.3486
99 | 36.49 | 6883.0994 | 13573.0897
99.1 | 36.53 | 6897.0785 | 13602.8634
99.2 | 36.57 | 6911.0706 | 13632.6697
99.3 | 36.6 | 6921.5733 | 13655.0459
99.4 | 36.64 | 6935.5882 | 13684.9093
99.5 | 36.68 | 6949.6162 | 13714.8053
99.6 | 36.71 | 6960.1458 | 13737.2487
99.7 | 36.75 | 6974.1966 | 13767.2018
99.8 | 36.79 | 6988.2604 | 13797.1876
99.9 | 36.82 | 6998.8168 | 13819.6983
100 | 36.86 | 7012.9035 | 13849.7411
125 | 46.08 | 10603.4683 | 21644.9174
150 | 55.29 | 14859.0985 | 31161.9174
175 | 64.51 | 19771.0717 | 42421.4077
200 | 73.72 | 25313.9699 | 55398.9643
225 | 82.94 | 31487.3088 | 70122.7686
250 | 92.15 | 38266.8811 | 86560.8818
275 | 101.37 | 45657.8841 | 104749
300 | 110.58 | 53635.8118 | 124647.6697
325 | 119.8 | 62210.3481 | 146300.1019
350 | 129.01 | 71355.9628 | 169659.3282
375 | 138.23 | 81086.1643 | 194776.0744
400 | 147.44 | 91374.0042 | 221595.8573
425 | 156.66 | 102236.4054 | 250176.9174
450 | 165.87 | 113644.7705 | 280457.2569
475 | 175.09 | 125619.1615 | 312502.631
500 | 184.3 | 138129.1899 | 346243.527
525 | 193.52 | 151197.8613 | 381753.2151
550 | 202.73 | 164792.9047 | 418954.6677
575 | 211.95 | 178940.1237 | 457928.6697
600 | 221.16 | 193605.3059 | 498590.6789